## Aircraft Maintenance Hgr
LEED v4 for BD+C: New Construction and Major Renovation
Project Checklist
Comply with Army Sustainable Design and Development Policy Update dated Jan 17, 2017
Compliance with UFC 1-200-02 and minimum LEED V4 Silver Level TPC are required. Reference Army Sustainability Implementation Guide dated 28 Feb 2023 for additional guidance.
https://rfpwizard.mrsi.erdc.dren.mil/MRSI/content/sustain/Library/Policy%20and%20Guidance/ Army%20Sustainability%20Implementation%20Guide_JAN23.pdf
Project Name: Standard Design Maintenance Hangar
Date: Sept. 2023
Y | ? | N |  |  |  |  | Discussion based on LEED V4 updated July 15, 2019
1 |  |  | Credit 1 | Integrative Process |  | 1 | This credit should be readily achievable for Hangars. - Preplanning will be required on energy and water related systems.
2 | 2 | 12 | Location and Transportation |  | Possible Points: | 16 | - The maximum points achievable under this category is 16, not 32. A project achieving credit 1 cannot achieve any credit from 2 through 8.
|  |  | Credit 1 | LEED for Neighborhood Development Location |  | 16 | These credits are not achievable for hangars. It's highly unlikely that a hangar will be built in a LEED Neighborhood Development location.
1 |  |  | Credit 2 | Sensitive Land Protection |  | 1 | This credit should be readily achievable for hangars. - Option 1: Locate on previously developed land. - Option 2: Do not build on Prime farmland Flood plains Habitat for threatened or endangered species (NatureServe) within 100 feet of water body within 50 feet of wetlands
|  | 2 | Credit 3 | High Priority Site |  | 2 | This credit is not readily achievable for hangars. Hangar are usually located next to airfield which might or might not be in a historic district or a brownfield site. - Option 1: Locate in historic district (1 point) - Option 2: Locate the project on (1 point) EPA national priority list Fed Empowerment Zone Fed Renewal Community site Dept of Treasure low-income community - Option 3: Brownfield Remediation
|  | 5 | Credit 4 | Surrounding Density and Diverse Uses |  | 5 | This credit is not readily achievable for hangars. Hangars are usually not built within 1/4 mile of high density areas or within 1/2 mile of diverse use spaces. - Option 1: Surrounding Density (2-3 points) Locate within 1/4 mile radius of high density areas - Option 2: Diverse Use (1-2 points) Locate within 1/2 mile walking distance to existing publicly available diverse use
|  | 5 | Credit 5 | Access to Quality Transit |  | 5 | This credit is not readily achievable for hangars. - 1/4 mile walking to transit stops (72 weekday trips and 40 weekend trips = 1 point; 144 weekday trips and 108 weekend trips=3 points; 360 weekday trips and 216 weekend trips=5 points) - 1/2 mile walking to rapid transit, rail, or ferry terminal For military projects, exception applies to on-site mass transit, but off post transit has to comply with requirements.
| 1 |  | Credit 6 | Bicycle Facilities |  | 1 | This credit maybe achievable for hangar projects. - locate within 200 yards biking distance to bicycle network that connects to one of the following at least 10 diverse uses a rapid transit stop, rail station, or ferry terminal - All destinations must be within 3 miles of project boundary. - Short-term Bicycle storage for 2.5% of peak visitors, not less than 4
1 |  |  | Credit 7 | Reduced Parking Footprint |  | 1 | This credit is achievable for hangar projects. - Do not exceed local code requirements for # of parking.
| 1 |  | Credit 8 | Green Vehicles |  | 1 | This credit is achievable for hangar projects. - 5% of overall parking stalls for green vehicles; and out of the 5%, 2% with charging station.
7 | 0 | 3 | Sustainable Sites |  | Possible Points: | 10
Y |  |  | Prereq 1 | Construction Activity Pollution Prevention |  | Required | Create and implement an erosion and sedimentation control plan for all construction activities associated with the project.
1 |  |  | Credit 1 | Site Assessment |  | 1 | This credit is readily achievable for hangar projects. Site survey or assessment to include - Topography: unique topo features and slope stability risks - Hydrology: Flood hazard area, delineate wetlands, lakes, streams, shorelines, rainwater collection and reuse - Climate: Solar exposure, heat island effect potential, seasonal sun angle, prevailing winds, monthly precipitation and temperature ranges - Vegetation: Vegetation type, greenfield area, significant tree mapping, threatened or endangered species, unique habitat, invasive plant species - Soil: delineation of prime farmland, healthy soils, previous development, disturbed soil - Human use: Views, adjacent transportation, adjacent properties, construction recycle or reuse - Human Health effects: vulnerable population, physical activity opportunities, major sources of air pollution
|  | 2 | Credit 2 | Site Development--Protect or Restore Habitat |  | 2 | This credit is not readily achievable for hangar projects due to required clearances around runway, taxiway, aircraft parking, and other hardstand requirements. - Restore 30% native or adapted vegetation, or land trust financial support at $.40 per sf for total site area.
|  | 1 | Credit 3 | Open Space |  | 1 | Due to hardstand requirements, this credit is not readily achievable for hangar projects. - Accessible Outdoor space > 30% of total site area with outdoor social activity, garden space for visual interest, garden for food production, or elements of human interaction. A minimum of 25% of that outdoor space must be vegetated.
3 |  |  | Credit 4 | Rainwater Management |  | 3 | This credit is achievable for hangar projects. - 2 points: manage 95th percentile rainfall using LID or green infrastructure. - 98th percentile = 3 points
2 |  |  | Credit 5 | Heat Island Reduction |  | 2 | This credit is achievable for hangar projects. - Area of non-roof (x2) + Area of high reflectance roof (x1.33) + Area of Vegetated Roof (x1.33) > total paved area + total roof area; - or min 75% parking under cover.
1 |  |  | Credit 6 | Light Pollution Reduction |  | 1 | This credit is achievable for hangar projects - Meet uplight and light trespass requirements
6 | 5 | 0 | Water Efficiency |  | Possible Points: | 11
Y |  |  | Prereq 1 | Outdoor Water Use Reduction |  | Required | No irrigation or reduction by 30% baseline from peak watering month.
Y |  |  | Prereq 2 | Indoor Water Use Reduction |  | Required | Reduce water consumption by 20% from baseline. Fixture must be watersense labeled.
Y |  |  | Prereq 3 | Building-Level Water Metering |  | Required | Water meter for total potable water use.
2 |  |  | Credit 1 | Outdoor Water Use Reduction |  | 2 | This credit is readily achievable for hangar projects. - No irrigation or reduced irrigation by 50% from baseline.
3 | 3 |  | Credit 2 | Indoor Water Use Reduction |  | 6 | This credit is readily achievable for hangar projects. - 30% reduction for 2 points. - Design team can pursue incremental reduction up to 50% for 4 additional points.
| 2 |  | Credit 3 | Cooling Tower Water Use |  | 2 | This credit maybe achievable for hangar projects. - Meet maximum allowable concentrations of chemicals per cycle for up to 2 points.
1 |  |  | Credit 4 | Water Metering |  | 1 | This credit is achievable for hangar projects. - Meter two or more of subsystems to include Irrigation, indoor plumbing fixture and fittings, Domestic hot water, boiler exceeding 100,000 gallons aggregate, single boiler exceeding 500,000 BtuH, reclaim water, and/or other process water.
10 | 16 | 7 | Energy and Atmosphere |  | Possible Points: | 33
Y |  |  | Prereq 1 | Fundamental Commissioning and Verification |  | Required | Complete the following commissioning (Cx) process activities for mechanical, electrical, plumbing, and renewable energy systems and assemblies, in accordance with ASHRAE Guideline 0-2005 and ASHRAE Guideline 1.1–2007
Y |  |  | Prereq 2 | Minimum Energy Performance |  | Required | Demonstrate an improvement of 5% for new construction comparison against a baseline building that complies with Standard 90.1–2010, Appendix G
Y |  |  | Prereq 3 | Building-Level Energy Metering |  | Required
Y |  |  | Prereq 4 | Fundamental Refrigerant Management |  | Required | Do not use chlorofluorocarbon (CFC)-based refrigerants in new heating, ventilating, air-conditioning, and refrigeration (HVAC&R) systems.
3 | 3 |  | Credit 1 | Enhanced Commissioning |  | 6 | This credit is achievable for hangar projects. - Enhanced system commissioning (3 points), + monitoring-based commissioning (1 point), Envelope commissioning (2 points)
5 | 13 |  | Credit 2 | Optimize Energy Performance |  | 18 | 12 of 18 points under this credit are mandatory. The other 6 points are optional for the design team. - UFC 1-200-02 requires 30% energy consumption reduction from ASHRAE 90.1 baseline.
1 |  |  | Credit 3 | Advanced Energy Metering |  | 1 | This credit is achievable for hangar projects. Energy metering is typical to Army Installations, but not advanced metering.
|  | 2 | Credit 4 | Demand Response |  | 2 | This is not typical for Army Projects. Participate in an existing demand response (DR) program, enroll in a minimum one-year DR participation.
|  | 3 | Credit 5 | Renewable Energy Production |  | 3 | This credit may be achievable for hangar projects. Use of community renewable energy system is allowed. - 1%=1 point - 5%=2 points - 10%=3 points
1 |  |  | Credit 6 | Enhanced Refrigerant Management |  | 1 | This credit is achievable for hangar projects. Unique to each hangar. Results depend on system selection.
|  | 2 | Credit 7 | Green Power and Carbon Offsets |  | 2 | Purchase of Green Power is typically not allowed.
7 | 1 | 5 | Materials and Resources |  | Possible Points: | 13
Y |  |  | Prereq 1 | Storage and Collection of Recyclables |  | Required | Provide dedicated area for storage of mixed paper, corrugated cardboard, glass, plastics, and metals, + batteries, mercury-containing lamps, and electronic waste.
Y |  |  | Prereq 2 | Construction and Demolition Waste Management Planning |  | Required | Establish waste diversion goals for 5 materials.
|  | 5 | Credit 1 | Building Life-Cycle Impact Reduction |  | 5 | This credit is not readily achievable in hangar projects. Building and material reuse is not typically incorporated into a hangar design due to hangar clearance requirements. - Option 1. Historic Building Reuse = 5 points. - Option 2. Renovate Abandoned or blighted building = 5 points. - Option 3. Off site Building Material Reuse = 2-4 points. - Option 4. Whole-Building Life Cycle Assessment = 3 points.
2 |  |  | Credit 2 | Building Product Disclosure and Optimization - Environmental Product Declarations |  | 2 | This construction credit is achievable for hangar projects. - Option 1 Env Product Declaration (EPD) for 20 different products = 1 point - Option 2 Multi-attribute optimization = 1 point;
2 |  |  | Credit 3 | Building Product Disclosure and Optimization - Sourcing of Raw Materials |  | 2 | This construction credit is achievable for hangar projects. - Option 1. Use at least 20 products from five different manufacturers who publically release their raw material and extraction report = 1 point; - Option 2. 25% installed building product complying extended producer responsibility, bio-based material, certified wood product, material reuse, recycle content, and USGBC approved program = 1 point.
1 | 1 |  | Credit 4 | Building Product Disclosure and Optimization - Material Ingredients |  | 2 | This construction credit is achievable for hangar projects. - Option 1. Use at least 20 different products from five different manufacturers with publically available inventory of all ingredients, Health Product declaration, certified as cradle to cradle, or other USGBC approved program. = 1 point - Option 2. Use products that document their material ingredients optimization with Greenscreen V1.2 Benchmark, cradle to cradle certification, International Alternative Compliance Path, or USGBC approved program. = 1 point - Option 3. Manufacturer supply chain optimization = 1 point.
2 |  |  | Credit 5 | Construction and Demolition Waste Management |  | 2 | This construction credit is readily achievable for hangar projects. - Divert 50% and 3 material streams = 1 point. - Divert 75% and 4 material streams = 1 additional point
8 | 4 | 4 | Indoor Environmental Quality |  | Possible Points: | 16
Y |  |  | Prereq 1 | Minimum Indoor Air Quality Performance |  | Required | - Option 1. Meet the minimum requirements of ASHRAE Standard 62.1–2010 - Option 2.
Y |  |  | Prereq 2 | Environmental Tobacco Smoke Control |  | Required | Prohibit smoking inside the building.
1 | 1 |  | Credit 1 | Enhanced Indoor Air Quality Strategies |  | 2 | This credit is achievable in hangar projects. - Option 1. Enhanced IAQ Strategies = 1 point - Option 1. Additional Enhanced IAQ Strategies = 1 additional point
3 |  |  | Credit 2 | Low-Emitting Materials |  | 3 | This construction credit is achievable in hangar projects. - Option 1. by Product Category Calculations. = 1-3 points. - Option 2. by Budget Calculation Method = 1-3 points.
1 |  |  | Credit 3 | Construction Indoor Air Quality Management Plan |  | 1 | This construction credit is readily achievable in hangar projects. (SMACNA) IAQ Guidelines
1 | 1 |  | Credit 4 | Indoor Air Quality Assessment |  | 2 | This construction credit is readily achievable in hangar projects. - Option 1. Flush-out before occupancy or during occupancy = 1 point. - Option 2. Air Testing = 2 total points.
1 |  |  | Credit 5 | Thermal Comfort |  | 1 | This credit is readily achievable in hangar projects. - Option 1. Meet ASHRAE 55-2010 = 1 point, or - Option 2. Meet ISO and CEN standards = 1 point
1 | 1 |  | Credit 6 | Interior Lighting |  | 2 | This credit is readily achievable in hangar projects. - Option 1. Provide lighting control to 90% of occupants. = 1 point. - Option 2. Lighting quality = 1 additional point
| 1 | 2 | Credit 7 | Daylight |  | 3 | This credit is achievable in hangar projects. - Option 1. Simulation. Spatial daylight autonomy 55% = 2 total points; 75% = 3 total points - Option 2. Simulation. Illuminance Calculation 75% = 1 point; 90% = 2 total points - Option 3. Measured. 75%=2 total points; 90%=3 total points
|  | 1 | Credit 8 | Quality Views |  | 1 | This credit is not readily achievable in hangar projects. - Achieve direct line of sight for 75% of all regularly occupied floor area.
|  | 1 | Credit 9 | Acoustic Performance |  | 1 | This credit is not readily achievable in hangar projects. - minimize the maximum background noise level from HVAC system per 2011 ASHRAE.
3 | 3 | 0 | Innovation |  | Possible Points: | 6
2 | 3 |  | Credit 1 | Innovation |  | 5 | This credit includes innovation option (up to 4 points), pilot credit option (up to 4 points), and exemplary performance option (up to 2 points). Total cannot exceed 5 points. Project team to determined credits to pursue.
1 |  |  | Credit 2 | LEED Accredited Professional |  | 1 | This credit is readily achievable. At least one principal participant of the project must be LEED AP with specialty appropriate for project.
2 | 2 | 0 | Regional Priority |  | Possible Points: | 4
1 |  |  | Credit 1 | Regional Priority: Specific Credit |  | 1 | Regional Priority Credit is geographically specific. Design team can earn up to 4 of the 6 regional priority credits. Design team needs to be familiar with regional priority credits for the specific location.
1 |  |  | Credit 2 | Regional Priority: Specific Credit |  | 1 | Regional Priority Credit is geographically specific. Design team can earn up to 4 of the 6 regional priority credits. Design team needs to be familiar with regional priority credits for the specific location.
| 1 |  | Credit 3 | Regional Priority: Specific Credit |  | 1 | Regional Priority Credit is geographically specific. Design team can earn up to 4 of the 6 regional priority credits. Design team needs to be familiar with regional priority credits for the specific location.
| 1 |  | Credit 4 | Regional Priority: Specific Credit |  | 1 | Regional Priority Credit is geographically specific. Design team can earn up to 4 of the 6 regional priority credits. Design team needs to be familiar with regional priority credits for the specific location.
46 | 33 | 31 | Total |  | Possible Points: | 110
Certified 40 to 49 points Silver 50 to 59 points Gold 60 to 79 points Platinum 80 to 110
Total of 46 points are readily achievable in hangar projects.
To achieve a total of 50 points for silver level certification, the design team needs to determine which additional 4 points out of 33 point to attempt.
A total of 31 points have been identified as not achievable in hangar projects.